## Wire Calculator
GUAGE for AL | OHMS PER 1K FEET | GUAGE for CU | OHMS PER 1K FEET | CALCULATOR
2000 | 0.0106 | 2000 | 0.00662 | GUAGE | TEST RESISTANCE in OHMS by meter | Run Length in ft | Amps to run through
1750 | 0.0121 | 1750 | 0.00756 | 14 | 0.4 | 200 | 20
1500 | 0.0141 | 1500 | 0.00883
1250 | 0.0169 | 1250 | 0.0106 | OUTPUT TEST LENGTH IN FT |  |  | Resistance of wire based on run length
1000 | 0.0212 | 1000 | 0.0132 | 122.6994 | FT of COPPER |  | 0.652 | Copper
900 | 0.0235 | 900 | 0.0147 | 77.3694 | FT of ALUMINUM |  | 1.034 | Aluminium
800 | 0.0265 | 800 | 0.0166
750 | 0.0282 | 750 | 0.0176 | VOLTAGE DROP over single phase run (round)
700 | 0.0303 | 700 | 0.0189 | 26.08 | Based on run Length
600 | 0.0353 | 600 | 0.0223 | 16 | Based on test Length Resistance | and amps
500 | 0.0424 | 500 | 0.0265 | 41.36 | Based on run Length
400 | 0.0529 | 400 | 0.0331
350 | 0.0605 | 350 | 0.0382
300 | 0.0707 | 300 | 0.0446
250 | 0.0847 | 250 | 0.0535 | VOLTAGE DROP over 3 phase phase run (round)
4/0 | 0.1 | 4/0 | 0.0626 | 22.5859 | Based on run Length
3/0 | 0.126 | 3/0 | 0.079 | 13.8564 | Based on test Length Resistance | and amps
2/0 | 0.159 | 2/0 | 0.101 | 35.8188 | Based on run Length
1/0 | 0.201 | 1/0 | 0.127
1 | 0.253 | 1 | 0.16
2 | 0.319 | 2 | 0.201 | VOLTAGE DROP over one cable one way
3 | 0.403 | 3 | 0.254 | 13.04 | Based on run Length
4 | 0.508 | 4 | 0.321 | 8 | Based on result of resistance test | and amps
6 | 0.808 | 6 | 0.51 | 20.68 | Based on run Length
8 | 1.28 | 8 | 0.809
10 | 2.04 | 10 | 1.29
12 | 3.25 | 12 | 2.05 | key: | Note
14 | 5.17 | 14 | 3.26 |  | Based on the test result
16 | 8.21 | 16 | 5.29 |  | Based on the inputted run length
18 | 13.1 | 18 | 8.45

## Conduit fill quick take
TABLE DATA | Fill amount allowed by code NEC 2020
CONDUIT | EMT | ENT | FMC | IMC | LFNC | RMC | PVC Schedule 80 | PVC Schedule 40 | PVC Type A | PVC Type B
3/8 | --- | --- | 0.046 | --- | 0.074 | --- | --- | --- | --- | ---
1/2 | 0.122 | 0.114 | 0.127 | 0.137 | 0.121 | 0.125 | 0.087 | 0.114 | 0.154 | ---
3/4 | 0.213 | 0.203 | 0.213 | 0.235 | 0.209 | 0.22 | 0.164 | 0.203 | 0.26 | ---
1 | 0.346 | 0.333 | 0.327 | 0.384 | 0.333 | 0.355 | 0.275 | 0.333 | 0.434 | ---
1 1/4 | 0.598 | 0.581 | 0.511 | 0.659 | 0.59 | 0.61 | 0.495 | 0.581 | 0.707 | ---
1 1/2 | 0.814 | 0.794 | 0.743 | 0.89 | 0.789 | 0.829 | 0.684 | 0.794 | 0.929 | ---
2 | 1.342 | 1.316 | 1.307 | 1.452 | 1.298 | 1.363 | 1.15 | 1.316 | 1.459 | 1.55
2 1/2 | 2.343 | --- | 1.963 | 2.054 | 1.953 | 1.946 | 1.647 | 1.878 | 2.181 | ---
3 | 3.538 | --- | 2.827 | 3.169 | 2.99 | 3 | 2.577 | 2.907 | 3.278 | 3.484
3 1/2 | 4.618 | --- | 3.848 | 4.234 | 3.893 | 4.004 | 3.475 | 3.895 | 4.278 | 4.546
4 | 5.901 | --- | 5.027 | 5.452 | 5.077 | 5.153 | 4.503 | 5.022 | 5.489 | 5.779
5 | --- | --- | --- | --- | --- | 8.085 | 7.142 | 7.904 | --- | 8.878
6 | --- | --- | --- | --- | --- | 11.663 | 10.239 | 11.427 | --- | 12.612
Size | 40% | 40%2 | 40%4 | 40%6 | 40%8 | 40%10 | 40%12 | 40%14 | 40%16 | 40%18
WIRE TYPE/GUAGE | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000 | 1250 | 1500 | 1750 | 2000
THHN | 0.0097 | 0.0133 | 0.0211 | 0.0366 | 0.0507 | 0.0824 | 0.0973 | 0.1158 | 0.1562 | 0.1855 | 0.2223 | 0.2679 | 0.3237 | 0.397 | 0.4608 | 0.5242 | 0.5863 | 0.7073 | 0.8676 | 0.9887 | 1.0496 | 1.1085 | 1.2311 | 1.3478
XHHW | 0.0139 | 0.0181 | 0.0243 | 0.0437 | 0.059 | 0.0814 | 0.0962 | 0.1146 | 0.1534 | 0.1825 | 0.219 | 0.2642 | 0.3197 | 0.3904 | 0.4536 | 0.5166 | 0.5782 | 0.6984 | 0.8709 | 0.9923 | 1.0532 | 1.1122 | 1.2351 | 1.3519 | 1.718 | 2.0156 | 2.3127 | 2.6073
DATA ENTRY
Fit chart -> number | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000 | 1250 | 1500 | 1750 | 2000
THHN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XHHW | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Conduit choice |  | Will it fit? | Available room in coduit |  | Total number of conductors
Type | Size | 40% | 100% -> | 2.0725 | Total -> | 3
RMC | 1 1/2 | YES
continue to results